## Main
Wire Size Calculation
This spreadsheet has 3 sections. The first section uses the data as determined by the power spreadsheet.
This will then calculate the resistance and the voltage drop. The main reason we calculate all this stuff
And it's usually much colder that that around here that all winter. The second section is to make the same
Calculation, but by plugging in the values yourself. The third section is a much simplified version to help
calculate wiring for non PV applications. The places you enter data are purple.
Array Data |  |  |  | Standalone Calculation
| Open Circuit Voltage | 43.1 |  |  | Open Circuit Voltage | 43.1
| Short Circuit current of panel | 5.46 |  |  | Short Circuit current of panel | 5.46
| Cold Weather factor (-40F) | 1.25 |  |  | Cold Weather factor (-40F) | 1.25
| True Amperage per panel | 6.83 |  |  | True Amperage per panel | 6.825
| Number of panels in series | 2 |  |  | Number of panels in series | 2
| Number of parallel strings | 6 |  |  | Number of parallel strings | 6
| Series Per Wire Run | 4 |  |  | Series Per Wire Run | 6
| Total Array Amperage | 51.19 |  |  | Total Array Amperage | 51.1875
| Max Array Voltage | 107.75 |  |  | Max Array Voltage | 107.75
| Max Wire Run Amperage | 34.1267 |  |  | Max Wire Run Amperage | 51.1875
| Max Wire Run Voltage | 71.8333 |  |  | Max Wire Run Voltage | 107.75
| Max Wire Ampacity | 42.5867 |  |  | Max Wire Ampacity | 63.882
| AWG Wire Gauge | 2 |  |  | AWG Wire Gauge | 1/0
| Distance | 135 |  |  | Distance | 130
| Voltage | 48 |  |  | Voltage | 48
| Temperature | 90 |  |  | Temperature | 50
| Temp Factor for Copper | 0.00323 |  |  | Temp Factor for Copper | 0.00323
| Temp Change Factor | 1.0485 |  |  | Temp Change Factor | 0.91925
| Resistance From NEC Table 8 | #N/A |  |  | Resistance From NEC Table 8 | 0.11215
| Voltage Loss | #N/A |  |  | Voltage Loss | 1.8627
| Voltage Drop | #N/A | #N/A |  | Voltage Drop | 3.881% | OK
Non PV Wiring
| Amperage | 20
| Wire Ampacity | 31.2
| AWG Wire Gauge | 8
| Distance | 10
| Voltage | 24
| Temperature | 120
| Temp Factor for Copper | 0.00323
| Temp Change Factor | 1.1454
| Resistance From NEC Table 8 | #N/A
| Voltage Loss | #N/A
| Voltage Drop | #N/A | #N/A
Notes:
The formula for adjusting NEC table 8 for temperature is as follows:
R2 = R1 [1 + acu(T2 – 75F)] where Acu = 0.00323
Note on D17: Enter the number of parallel strings for each wire run.
Note on D23: Enter the AWG wire gauge you wish to use.
Note on D24: Enter the distance between the PV panel combiner box and the charge controller.
Note on D25: Enter the voltage of the wire run between the PV panels and the charge controller.
Note on D26: Enter the lowest or highest Operating temperature. This effects the resistance.
Note on D37: Enter the AWG wire gauge you wish to use.
Note on D38: Enter the distance between the PV panel combiner box and the charge controller.
Note on D39: Enter the voltage of the wire run between the PV panels and the charge controller.
Note on D40: Enter the lowest or highest Operating temperature. This effects the resistance.
Note on I11: Enter the max open circuit voltage of the panel.
Note on I12: Enter the short circuit current of the panel.
Note on I15: Enter the number of panels in a series string.
Note on I16: Enter the number of parallel strings.
Note on I17: Enter the number of parallel strings for each wire run.
Note on I23: Enter the AWG wire gauge you wish to use.
Note on I24: Enter the distance between the PV panel combiner box and the charge controller.
Note on I25: Enter the voltage of the wire run between the PV panels and the charge controller.
Note on I26: Enter the lowest or highest Operating temperature. This effects the resistance.

## VoltDrop
Voltage drop
|  | NEC Table 8 | [5 empty] | NEC Table 8
| DC Resistance at 167F, 1000 feet, stranded | [5 empty] | DC Resistance at 167F, 1000 feet, solid
AWG | Conductors | Area Cir. | Copper | Copper |  | AWG | Area Cir. | Copper | Copper
|  | Mils | Uncoated | Coated |  |  | Mils | Uncoated | Coated
18 | 7 | 1620 | 7.95 | 8.45 | 0.00845 | 18 | 1620 | 7.77 | 8.08 | 0.00808
16 | 7 | 2580 | 4.99 | 5.29 | 0.00529 | 16 | 2580 | 4.89 | 5.08 | 0.00508
14 | 7 | 4110 | 3.14 | 3.26 | 0.00326 | 14 | 4110 | 3.07 | 3.19 | 0.00319
12 | 7 | 6530 | 1.98 | 2.05 | 0.00205 | 12 | 6530 | 1.93 | 2.01 | 0.00201
10 | 7 | 10380 | 1.24 | 1.29 | 0.00129 | 10 | 10380 | 1.21 | 1.26 | 0.00126
8 | 7 | 16510 | 0.778 | 0.809 | 0.000809 | 8 | 16510 | 0.764 | 0.786 | 0.000786
6 | 7 | 26240 | 0.491 | 0.51 | 0.00051
4 | 7 | 41740 | 0.308 | 0.321 | 0.000321
3 | 7 | 52620 | 0.245 | 0.254 | 0.000254 |  | Correction Factor for Crystalline Panels
2 | 7 | 66360 | 0.194 | 0.201 | 0.000201
1 | 19 | 83690 | 0.154 | 0.16 | 0.00016 | High Temp | Low Temp | Factor
1/0 | 19 | 105600 | 0.122 | 0.127 | 0.000127 | 77 | 50 | 1.06
2/0 | 19 | 133100 | 0.0967 | 0.101 | 0.000101 | 49 | 32 | 1.1
3/0 | 19 | 167800 | 0.0766 | 0.0797 | 7.97e-05 | 31 | 14 | 1.13
4/0 | 19 | 211600 | 0.0608 | 0.608 | 0.000608 | 13 | -4 | 1.17
[6 empty] | -5 | -40 | 1.25
Circuit Resistance
| Battery @ 12VDC |  | 0.0015
| Battery @ 24VDC |  | 0.003
| Battery @ 48VDC |  | 0.006
| Battery contacts |  | 0.0016
| Inverter contacts |  | 0.0004
| Breaker |  | 0.002
| Conductors |  | 0.0024
Drop = Current in Amps x resistance per foot x length
Voltage drop= Amp x ohms

## NewPanels
New Panels Project
| Size | Quantiy | Cost | Total
PV Panels | 165 | 12 | 545 | 6540
PV Rack | 12 Panels | 2 | 269 | 538
7078
#2 AWG | 500' | 1 | 175 | 175 | Colotex Electric
#10AWG/2 | 500' | 1 | 30.38 | 30.38
#Cat 5e | 1000' | 2 | 51.3 | 102.6
#14AWG Speaker | 500' | 1 | 14.7 | 14.7
#2 Bare Ground | 250' | 1 | 31.25 | 31.25
322.68
PVC Pipe | 1.5 | 14 | 3.29 | 46.06 | Home Depot
90 Elbows | 1.5 | 2 | 1.99 | 3.98
45 Elbows | 1.5 | 3 | 1.69 | 5.07
Male Thread | 1.5 | 2 | 0.59 | 1.18
Access Fitting | 1.5 | 1 | 5.94 | 5.94
Coupling | 1.5 | 1 | 0.59 | 0.59
Locknut | 1.5 | 1 | 0.66 | 0.66
63.48
PVC Pipe | 0.75 | 14 | 1.17 | 16.38
90 Elbows | 0.75 | 2 | 0.75 | 1.5
45 Elbows | 0.75 | 3 | 0.65 | 1.95
Male Thread | 0.75 | 2 | 0.37 | 0.74
Access Fitting | 0.75 | 1 | 2.99 | 2.99
Coupling | 0.75 | 1 | 0.75 | 0.75
Locknut | 0.75 | 1 | 0.24 | 0.24
24.55
Combiner Box
30A Fuse Block | 75747 | 3 | 9.82 | 29.46 | Colotex Electric
8A Fuses | 74778 | 5 | 4.49 | 22.45
Isolated Ground Kit | 15850 | 2 | 7.5 | 15
Equip Ground, 12 lugs | 15846 | 2 | 2.03 | 4.06
Lugs #6-2/0 | 15843 | 2 | 3.3 | 6.6
NEMA 3R Box (8x12) |  | 1 | 23.16 | 23.16
Delta Lightening Arrestor |  | 1 | 39 | 39
139.73
PV Subtotal |  |  |  | 7078
PVC Subtotal |  |  |  | 88.03
Wire Subtotal |  |  |  | 322.68
Combiner Box |  |  |  | 24.55
Total |  |  |  | 7513.26
Junction Box (6x6x4) |  | 1 | 10.95 | 10.95
Note on C15: 5 foot sections
Note on C24: 5 foot section